## Slide 1: Small Hydro

## Slide 2
OUTLINE
Hydropower Plants
Classifications
Different Layouts of Hydropower Plants
Concept of Power Generation
Hydro turbines

## Slide 3
Hydropower Plants
Hydropower plant uses potential energy of water.
It converts potential energy into electrical energy.
It is renewable form of energy.
Application of hydropower plants:
Generation of electric power.
Storage of irrigation water.
Control of floods in the river.
Storage of drinking water supply.

## Slide 4
Sardar Sarovar
Kadana
Hydropower Plants in India

## Slide 5: Hydropower Plants in Gujarat
Name of Plant | River - District | Capacity | Type of Turbine
Sardar Sarovar | Narmada - Narmada | 6 x 200 MW = 1200 MW 5 x 50 MW = 250 MW 1450 MW | Reversible Francis Kaplan
Ukai | Tapi – Surat & Tapi | 4 x 75 MW = 300 MW | Kaplan
Kadana | Mahi - Mahisagar | 4 x 60 MW = 240 MW | Reversible Francis (2) Francis (2)

## Slide 6: 2. Classifications
Dependent on Capacity:
Depending on Head:
Size | Unit size
Micro | Upto 100 kW
Mini | 101 to 1000 kW
Small | 1 to 25 MW
Ultra low head | Below 3 m
Low head | Less than 30 m
Medium head | Between 30 to 75 m
High head | Above 75 m

## Slide 7
Layouts of Dam based Hydropower Plant (Front view)
3. Different Layouts of Hydropower Plants

## Slide 8
Layouts of Dam based Hydropower Plant (Side view)

## Slide 9
Layouts of Canal based Hydropower Plant

## Slide 10
Layouts of River based Hydropower Plant

## Slide 11: Major Components of a Hydropower Plants
Diversion and intake
Desilting chamber
Water conductor system
Forebay / balancing reservoir
Surgetank
Penstock
Powerhouse – turbine, generator etc.
Tail race channel

## Slide 12
4. Concept of Power Generation

## Slide 13
CLASSIFICATION OF TURBINES
Impulse
Reaction
Pelton turbine
Axial Flow
Kaplan turbine
Bulb turbine
Tube turbine
Straflo turbine
Mixed Flow
Francis turbine
5. Hydro Turbines

## Slide 14
Suitability of Turbines
Turbine | Principle | Type of flow | Head | Discharge | Specific speed
Pelton | Impulse | Tangential | High | Low | Low
Francis | Reaction | Mixed (radial entry, axial exit) | Medium | Medium | Medium
Kaplan | Reaction | Axial | Low | High | High

## Slide 15
Impulse Turbine
All the pressure energy is converted into kinetic energy in Nozzle and then pressure remains constant.
Reaction Turbine
As water passes through the casing the pressure to kinetic energy conversion took place gradually.
The work is done on the blades by the combined effects of impulse and reaction.

## Slide 16
Pelton Turbine
Impulse turbine
Tangential flow
For high head
& low discharge
For low specific speed

## Slide 17: Main Components
Runner (wheel)
Buckets
Nozzle
Spear (valve)
Casing
Braking nozzle
Governing mechanism

## Slide 18
Pelton Wheel

## Slide 19: Main components
Francis is inward flow reaction or mixed flow type
It is used for medium head, medium discharge and medium specific speed.
Francis Turbine
[Stay vanes are optional]
Runner with runner vanes
Guide vanes (with guide wheel)
Spiral Casing
Draft tube

## Slide 20
FRANCIS TURBINE – Vertical axis

## Slide 21
1 | GENERATOR
2 | SPIRAL CASING
3 | BEARING HOUSING
4 | DRAFT TUBE BEND
5 | DRAFT TUBE
6 | COUPLING
7 | BUTTERFLY VALVE
FRANCIS TURBINE – Horizontal axis

## Slide 22
Installation of Francis turbine runner

## Slide 23
Kaplan Turbine

## Slide 26
Installation of Kaplan turbine propeller

## Slide 27: Main components
Propeller with movable blades
Guide vanes (or Wicket gates)
Spiral Casing
Draft tube

## Slide 28
Bulb Turbine

## Slide 30
Tubular Turbine

## Slide 31
Straflow Turbine
The Straflo turbine is a type of reaction turbine that is used in low to medium-head applications, typically ranging from 3 to 50 meters.

## Slide 32
THANK YOU